## Register List
Sr. No | Category | Reg Type | Reg Type | Address | Abs Address | Unique ID | R/W | Display Setting Number | Memory Type | Name | Type / Unit | Range | Scale | Default | Description | Profile 1 Future Use | Profile 2 Future Use | Profile 3 Future Use | Profile 4 Future Use | Profile 5 Future Use | Profile 6 Future Use | Profile 7 Future Use | Profile 8 Future Use | Profile 9 Future Use | Profile 10 Future Use | Profile 11 Future Use | Profile 12 Future Use | Profile 13 Future Use | Profile 14 Future Use | Profile 15 Future Use | Profile 16 Future Use
1 | Device | l Input | v setup | 0 | 30001 | DVC001 | R | NA | F | Device Type | int | Future Use | 1 | 1 | Future Use
2 | Device | l Input | v setup | 1 | 30002 | DVC002 | R | 0 | F | Firmware Version part 1 | 2 bytes | 0-255 . 0-255 | 1 | 1.02 | 1.2 (Firmware version: major. Minor)
3 | Device | l Input | v setup | 2 | 30003 | DVC003 | R | 1 | F | Firmware Version part 2 | 2 bytes | 0-255 . 0-255 | 1 | 01.00 | 1.0 (Firmware version: bug. Build)
4 | Device | l Input | £ runtime | 3 | 30004 | DVC004 | R | NA | V | Device faults | bitmap | Bit 0: (Reserved) Bit 1: On-board sensor fault Bit 2: External sensor fault Bit 3: Port1 Modbus loss of comms Bit 4: Port2 receive timeout (DALI64) Bit 5: Setpoint min/max mismatch Bit 6: Fan Speed min/max mismatch Bit 7: Lights min/max mismatch Bit 8: Blinds min/max mismatch | 1 | 0 | For onboard sensor: Valid Range Temp 0-80°C, Rh 0-100% Valid ranges for external sensor ( fault in case out side range) NTC sensors: -10…..+60 °C 0-10V : 0….11 V 2-10V: 1.5…..11 V Incorrect Min Max value
5 | Device | l Input | £ runtime | 4 | 30005 | DVC005 | R | NA | V | Override Status | bitmap | Bit0: Setpoint changed from default Bit1: Fan speed overridden (not auto) Bit2: HVAC mode overridden Bit3: {reserved} Bit4: Occupancy overridden Bit5: DnD active Bit6: MuR active | 1 | 0
6 | Device | l Input | £ runtime | 5 | 30006 | DVC006 | R | NA | V | External sensor measured value | Ω °C % - | Raw ohms range 3000-72000 (resolution 135 Ohm @ 20 K) Temperature range 0-50°C | 1 0.1 1 1 | 0 | Unit & Scale depend on signal type: Raw Ohms: unit= Ω, scale = 1 NTC: unit = °C, scale = 0.1 0(2)-10Vdc: unit = Percent, scale = 0.1 NO : 0=open, 1 = closed NC : 0=closed, 1 = open
7 | Device | l Input | £ runtime | 6 | 30007 | DVC007 | R | NA | V | On-board sensor temp | °C | 0-50 °C | 0.1
8 | Device | l Input | £ runtime | 7 | 30008 | DVC008 | R | NA | V | On-board humidity sensor | %Rh | 0..100% | 1
9 | Device | l Input | £ runtime | 8 | 30009 | DVC009 | R | NA | V | Did Mur status | enum | 0: none 1: DnD 2: MuR | 1 | 0
10 | Device | l Input | £ runtime | 9 | 30010 | DVC029 | R | NA | V | What has changed | bitmap | Bit0: Setpoint Bit1: Fan speed Bit2: HVAC mode Bit3: {reserved} Bit4: Occupancy Bit5: DnD/Mur Bit6: {reserved} Bit7: {reserved} Bit8: Light group 1 Bit9: Light group 2 Bit10: Light group 3 Bit11: Light group 4 Bit12: Blind 1 Bit13: Blind 2 | 1 | 0 | Automatically resets to 0 when master reads this
11 | Device | l Holding | £ runtime | 1000 | 41001 | DVC010 | R/W | NA | V | Override Reset | bitmap | Bit0: Reset Setpoint (1) Bit1: Reset Fan Speed to AUTO (2) Bit2: Clear HVAC mode override (4) Bit3: Clear Occupancy Override except Holiday (8) Bit4: Clear Occupancy Override including Holiday (16) Bit5: Clear DnD (32) Bit6: Clear MuR (64) Bit7: Reset temperature unit to configured unit - UI017 (128) Bit8: Clear ECO (256) ... Bit15: Reset WM (32768) | 1 | 0 | This register is edge triggered. WM resets the relevant property on the rising edge of the related bitfield. Bit15 means Restart of the device (like a power up)
12 | Device | l Coil | v setup | 0 | 1 | DVC011 | W | NA | V | Save Changes | bool | 0/1 |  | 0 | Edge triggered Save configuration parameters to Flash on Rising edge ( 0 to 1) Automatically resets to "0" after save
13 | Device | [6 empty] | 999 | V | Reset Modbus Setting |  | Future Use (Use Factory Reset Instead) | - | 0 | Future Use (Use Factory Reset Instead)
14 | Device | l Holding | v setup | 2000 | 42001 | DVC013 | R/W | 2 | NV | Config Id | int | 0-65535 (future use for Profiles) | 1 | 0 | Reserved for future to select a templates / Profiles) | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
15 | Device | l Holding | v setup | 2001 | 42002 | DVC014 | R/W | 3 | NV | Config Date Code | 2 bytes | 21-99 ; 1-52 | 1 | 0 | Date of device configuration can be stored here (optional) Last two digits of calendar year (21-99) Week of the year (1-52)
16 | Device | l Holding | v setup | 2002 | 42003 | DVC015 | R/W | 4 | NV | Modbus slave address | int | 1-247 | 1 | 2 | Should be different from DALI64 address on Port 2 (if any) | y |  |  |  |  | y |  |  |  |  | y |  | y
17 | Device | l Holding | v setup | 2003 | 42004 | DVC016 | R/W | 5 | NV | Port1 Baudrate | enum | 0: 1200 baud 1: 2400 baud 2: 4800 baud 3: 9600 baud 4: 14400 baud 5: 19200 baud 6: 38400 baud 7: future Use 8: future Use | 1 | 5 | (Default 19200 baud) | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
18 | Device | l Holding | v setup | 2004 | 42005 | DVC017 | R/W | 6 | NV | Port1 Parity | enum | 0: none 1: odd 2: even | 1 | 2 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
19 | Device | l Holding | v setup | 2005 | 42006 | DVC018 | R/W | 7 | NV | Port1 Stop Bits | int | 1-2 | 1 | 1 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
20 | Device | l Holding | v setup | 2006 | 42007 | DVC019 | R/W | 8 | NV | Port2 Baudrate | enum | 0: 1200 baud 1: 2400 baud 2: 4800 baud 3: 9600 baud 4: 14400 baud 5: 19200 baud 6: 38400 baud 7: future Use 8: future Use | 1 | 5 | (Default 19200 baud) | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
21 | Device | l Holding | v setup | 2007 | 42008 | DVC020 | R/W | 9 | NV | Port2 Parity | enum | 0: none 1: odd 2: even | 1 | 2 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
22 | Device | l Holding | v setup | 2008 | 42009 | DVC021 | R/W | 10 | NV | Port2 Stop Bits | int | 1-2 | 1 | 1 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
23 | Device | l Holding | v setup | 2009 | 42010 | DVC022 | R/W | 11 | NV | Port2 Response Timeout | msec | 200-3000 msec | 1 | 500 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
24 | Device | l Holding | v setup | 2010 | 42011 | DVC023 | R/W | 12 | NV | Dali64 sensor slave address on port 2 | int | 0-247 | 1 | 0 | Should be different from TR80 Modbus address 0 = No DALI sensor on port 2 (No repeater function) | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
25 | Device | l Holding | v setup | 2011 | 42012 | DVC024 | R/W | 13 | NV | External sensor type configuration | enum | 0: NONE 1: NO contact 2: NC contact 3: 0-10 Vdc 4: 2-10 Vdc 5: Raw Ohms 6: NTC10K 7: NTC20K | 1 | 0 | NO : 0=open, 1 = closed NC : 0= closed, 1 = open | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
26 | Device | l Holding | v setup | 2012 | 42013 | DVC025 | R/W | 14 | NV | On-board sensor temp offset | signed | -10.0 … +10.0 K | 0.1 | 0
27 | Device | l Holding | v setup | 2013 | 42014 | DVC026 | R/W | 15 | NV | On-board humidity sensor offset | signed | -10 … +10 %Rh | 1 | 0
28 | Device | l Holding | v setup | 2014 | 42015 | DVC027 | R/W | 16 | NV | DnD MuR enable | enum | 0: disabled 1: DnD enable 2: MuR enable 3: DnD and MuR both enabled | 1 | 1 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
28.5 | Device | l Holding | v setup | 2015 | 42016 | DVC028 | R/W | 17 | NV | Commissioning Mode Time | hours | 0-336 hours (14 days) | 1 | 0 | Device will not go to lock/Sleep mode for the duration configuration mode is active, this feature can be used during commissioning by installer. Configuration passkey will not be asked for this duration
30 | UI | l Input | £ runtime | 100 | 30101 | UI001 | R | NA | V | Active Display Mode | enum | 0: Dark Mode 1: Sleep Mode 2: Ready Mode 3: Protected Mode 4: Setting Mode (temp, light etc.) 5: Config Mode 6: Cleaning Mode 7: Passkey Entry Mode | 1 | - | Shows current display mode
31 | UI | l Input | £ runtime | 101 | 30102 | UI002 | R | NA | V | Cleaning Mode Status | enum | 0: Not in Cleaning mode 1: Cleaning mode | - | 0 | Shows if the device is in cleaning mode or not
32 | UI | l Input | £ runtime | 102 | 30103 | UI029 | R | NA | V | Power Button Action / Command | enum | 0: default 1: Lights On command activated 2: Lights Off command activated | 1 | 0 | Automatically resets to 0 when master reads this See power button function DV021 & DV022 for more details
33 | UI | l Holding | £ runtime | 1100 | 41101 | UI003 | R/W | NA | NV | LED ring colour | RGB565 | 0-65535 | 1 | 0 | 0 = Auto. See HV004. Ring colour normally changes according to heat/cool mode. The master will write to this register only when it needs to override automatic behavior
34 | UI | l Holding | £ runtime | 1101 | 41102 | UI004 | R/W | NA | NV | LED ring style | enum | 0: auto: Ring behaves according HV004 1: off 2: steady 3: slow breath 4: medium breath 5: fast breath 6: blink 7: fast blink | 1 | 0 | 0 = auto. See HV004 Ring color & style change automatically according to active Hvar Mode (heating=orange, cooling=blue…). This register gives the master controller the Additional ability to override style (blink, breath..).
35 | UI | l Holding | £ runtime | 1102 | 41103 | UI005 | R/W | NA | V | Window icon | enum | 0: off 1: on 2: blink | 1 | 0 | Controller can write to this register to enable window open Icon on wall module display.
36 | UI | l Holding | £ runtime | 1103 | 41104 | UI006 | R/W | NA | V | ECO icon | enum | 0: off 1: on 2: blink | 1 | 0 | If user selection enabled (UI032), this operates in last wins mode. Master override user selection.
37 | UI | l Holding | £ runtime | 1104 | 41105 | UI007 | R/W | NA | V | Alarm icon | enum | 0: off 1: on 2: blink 3: auto | 1 | 3 | In AUTO, alarm icon is activated from 'Device faults' register
38 | UI | l Holding | £ runtime | 1105 | 41106 | UI008 | R/W | NA | V | Day/Night icon | enum | 0: off 1: sun icon on 2: moon icon on 3: sun icon blink 4: moon icon blink | 1 | 0 | Day/night icons are now controlled by master. No internal logic connected to occupancy
39 | UI | l Holding | £ runtime | 1106 | 41107 | UI028 | R/W | NA | V | Text override | enum | 0: none 1: "Fan Off" 2: “Cooling/Heating Off” 3: "Window Open" 4: "Condensation" 5: "Fire" 6: "Service required" | - | 0 | This overrides text on upper 4 digit alphanumeric display on the wall module display when set
40 | UI | l Holding | v setup | 2100 | 42101 | UI009 | R/W | 100 | NV | Room Number | int | 0-9999 (or undefined = 0x7FFF) | 1 | 0x7FFF | Room Number can be stored here and will be available in Scrolling list (if undefined, = 0x7FFF, Skip from scrolling list )
41 | UI | l Holding | v setup | 2101 | 42102 | UI010 | R/W | NA | NV | Room Id1 | 2 x ascii | Future Use | 1 | 0
42 | UI | l Holding | v setup | 2102 | 42103 | UI011 | R/W | NA | NV | Room Id2 | 2 x ascii | Future Use | 1 | 0
43 | UI | l Holding | v setup | 2103 | 42104 | UI012 | R/W | 101 | NV | LCD Backlight brightness | % | 0…100% | 1 | 100% |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
44 | UI | l Holding | v setup | 2104 | 42105 | UI013 | R/W | 102 | NV | Ring brightness | % | 0…100% | 1 | 100% |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
45 | UI | l Holding | v setup | 2105 | 42106 | UI014 | R/W | 103 | NV | SLEEP mode ring brightness | % | 0…100% | 1 | 75% | To turn off LED ring in sleep mode, set this to 0% | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
46 | UI | l Holding | v setup | 2106 | 42107 | UI015 | R/W | 104 | NV | Room temperature display resolution | enum | 0: don't display room temp. 1: 1 deg resolution 2: 0.5 deg resolution 3: 0.1 deg resolution | 1 | 1 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
47 | UI | l Holding | v setup | 2107 | 42108 | UI016 | R/W | 105 | NV | Outdoor temperature display resolution | enum | 0: 1 deg resolution 1: 0.5 deg resolution 2: 0.1 deg resolution | 1 | 2 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
48 | UI | l Holding | v setup | 2108 | 42109 | UI017 | R/W | 106 | NV | Temperature unit & user change option |  | 0: °C (Default, use can change to °F ) 1: °F (Default, use can change to °C ) 2: °C (fixed, user cannot change) 3: °F (fixed, user cannot change) | 1 | 0 | Affects all displayed temperature values, including indoor, outdoor, setpoint... | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
49 | UI | l Holding | v setup | 2109 | 42110 | UI020 | R/W | 107 | NV | Cleaning Mode Time | sec | 10-7200 sec | 1 | 60 sec | Touch keys will remain locked for this duration in cleaning mode | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
50 | UI | l Holding | v setup | 2110 | 42111 | UI021 | R/W | 108 | NV | Power Button Short Press Function | enum | 0: No function 1: Dark Mode 2: Sleep Mode 3: SwitchLightsOnOffToggle 4: SwitchLightsOn 5: SwitchLightsOff 6: (Reserved for future) 7: (Reserved for future) 8: (Reserved for future) | 1 | 2 | 0 = Power button disabled in Ready Mode | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
51 | UI | l Holding | v setup | 2111 | 42112 | UI022 | R/W | 109 | NV | Power Button Long Press Function | enum | 0: No function 1: Dark Mode 2: Sleep Mode 3: SwitchLightsOnOffToggle 4: SwitchLightsOn 5: SwitchLightsOff 6: (Reserved for future) 7: (Reserved for future) 8: (Reserved for future) | 1 | 0 | 0 = Power button disabled in Ready Mode | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
52 | Access | l Holding | v setup | 2112 | 42113 | UI023 | R/W | 110 | NV | User Access Protection | enum | 0 free: no restriction, no timeout lock 1 simple: require key combination to unlock 2 secure: require pass-key to unlock 3 no access: display only, no control allowed | 1 | 0 | User access to change Temperature setpoint, Fan, Occupancy control Light and Blind etc. | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
53 | Access | l Holding | v setup | 2113 | 42114 | UI024 | R/W | 111 | NV | User Access Passkey | - | 0000…9999 | 1 | 0000 | Only used if User Access Protection = secure | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
54 | Access | l Holding | v setup | 2114 | 42115 | UI025 | R/W | 112 | NV | Config Menu Passkey | - | 0000…9999 | 1 | 4663 | To access configuration menu by installer Default 4663 (''HONE' on Numeric keypad) Do not forget to change on completion of installation | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
55 | UI | l Holding | v setup | 2115 | 42116 | UI026 | R/W | 113 | NV | Display Sleep Timeout | sec | 0…300 sec | 1 | 15 sec | If value is 0, display will always be on | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
56 | Access | l Holding | v setup | 2116 | 42117 | UI027 | R/W | NA | NV | Allow config | enum | 0: config not allowed 1: config allowed | - | 1 | Allow config parameter changes from device display | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
57 | UI | l Holding | v setup | 2117 | 42118 | UI030 | R/W | 114 | NV | LED Ring Timeout in Sleep Status | sec (signed) | 0…300 sec, -1=disabled | 1 | -1 | -1: LED ring always Active (Even in Sleep status) 0: Ring turns off immediately in sleep status 1-300Sec: Time delay for ring to go off in sleep status | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
58 | UI | l Holding | v setup | 2118 | 42119 | UI031 | R/W | 115 | NV | Departure Delay | sec | 0-300 sec | 1 | 10 sec | Used for power button functions (UI021 & UI022). Timer delay for Power Button light off command execution | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
58.5 | UI | l Holding | v setup | 2119 | 42120 | UI032 | R/W | 116 | NV | User ECO mode selection | enum | 0: disabled, 1: enabled | 1 | 0 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
59 | HVAC | l Input | £ runtime | 200 | 30201 | HV001 | R | NA | V | User Selected HVAC Mode (from Display) | enum | 0: auto 1: Heating 2: Cooling 3: Fan-only 4: Off 5: Heating 1 6: Heating 2 7: Cooling 1 8: Cooling 2 | 1 | 0
60 | Fan | l Input | £ runtime | 201 | 30202 | HV002 | R | NA | V | User Selected Fan speed (from Display) | % or int | EC Fans: 0..100% Others: 0..3 (Off-Lo-Med-Hi) Auto= 0x7FFF | 1 | 0x7FFF | if fan mode is auto, the value of this register is 0x7FFF and controller controls the fan speed
61 | Setpoint | l Input | £ runtime | 202 | 30203 | HV018 | R | NA | V | Temperature setpoint limited | signed int (°C / K) | as per HV008 and HV009 | 0.1
62 | Setpoint | l Holding | £ runtime | 1200 | 41201 | HV003 | R/W | NA | NV | User Selected Temperature Setpoint | signed int (°C / K) | as per HV008 and HV009 | 0.1
63 | HVAC | l Holding | £ runtime | 1201 | 41202 | HV004 | R/W | NA | V | Ring Behavior Depending on the cooling and heating coils status sent from controller (HVAC Mode and output active in master controller) | bitwise | Bits 0..2: (Used as enum) - 0: heat & cool not available (grey ring) - 1: Cooling mode Active (blue ring) - 2: Heating mode Active (orange ring) - 3: Heating + cooling Active (purple ring) - 4: Fan-only (green ring) Active - 5: Alarm (red ring) Active Bits 9..8 (only if Orange/Heating, means + value 2) - 0: All heat Outputs off (steady ring) - 256: Heat 1 Output on (slow breath) - 512: Heat 2 Output on (medium breath) - 768: All heat Outputs on (fast breath) Bits 11..10 (Only if blue/ Cooling, means + value 1) - 0: All cool outputs off (steady ring) - 1024: Cool 1 Output on (slow breath) - 2048: Cool 2 Output on (medium breath) - 3072: All cool outputs on (fast breath) Bit 12: Fan output on (slow breath - only if green) - 4096: Fan is running without Cooling and Heating outputs on | 1 | 0 | The ring shows the room user the status of cooling and heating in this room. A constant blue means that cooling mode is active, but is not currently switched on. A constant orange means that the heating mode is active, but is not currently switched on. The ring begins to breathe as soon as the room is cooled or heated. A breathing green means the fan is on with no cooling and no heating; as soon as the air in the room is circulated, a cooling effect occurs. Gray means that no cooling and no heating is currently possible; the central cooling and heating system is turned off or the room user has disabled cooling or heating via a HVAC Mode overwrite. Note: This register HV004 works only if UI004 (LED ring style) = Value 0 = Auto. Bit representation: 000D CCBB 0000 0AAA AAA (bits 2-0): currently active havoc mode info BB (bits 9-8): Heating outputs status CC (bits 11-10): Cooling outputs status D (bit 12): fan output status
64 | HVAC | l Holding | £ runtime | 1202 | 41203 | HV005 | R/W | NA | V | Fan Speed Active in Master Controller | int | EC Fans: 0..100% Others: 0..3 Unknown/invalid: 0x7FFF | 1 | 0x7FFF
65 | HVAC | l Holding | v setup | 2200 | 42201 | HV007 | R/W | 200 | NV | Setpoint Type | enum | 0: absolute 1: relative | 1 | 0: absolute |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
66 | HVAC | l Holding | v setup | 2201 | 42202 | HV008 | R/W | 201 | NV | Setpoint minimum | signed int (°C / K) | -50....+150 | 0.1 | 10 °C | Should be less than Max value | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
67 | HVAC | l Holding | v setup | 2202 | 42203 | HV009 | R/W | 202 | NV | Setpoint maximum | signed int (°C / K) | -50....+150 | 0.1 | 30 °C | Should be greater than min value | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
68 | HVAC | l Holding | v setup | 2203 | 42204 | HV010 | R/W | 203 | NV | Absolute Mode Default Setpoint | °C | -10....+40 | 0.1 | 22 °C |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
69 | HVAC | l Holding | v setup | 2204 | 42205 | HV011 | R/W | 204 | NV | Fan Type | enum | 0: no fan 1: Single speed fan 2: Two-speed fan 3: 3-speed fan 4: EC fan | 1 | 3 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
70 | HVAC | l Holding | v setup | 2205 | 42206 | HV012 | R/W | 205 | NV | EC Fan speed adjustment step size | enum | 0: 1% 1 : 2% 2 : 5% 3: 10% 4: 20% | 1 | 3: 10% | For EC fans only | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
71 | HVAC | l Holding | v setup | 2206 | 42207 | HV013 | R/W | 206 | NV | Fan speed low-limit | % or int | 0-100 | 1 | 0 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
72 | HVAC | l Holding | v setup | 2207 | 42208 | HV014 | R/W | 207 | NV | Fan speed high limit | % or int | 0-100 | 1 | 100 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
73 | HVAC | l Holding | v setup | 2208 | 42209 | HV015 | R/W | 208 | NV | Fan UI attributes | bitmap | Bit 0: Fan override 0: No User override 1: Allow override Bit 1: Display of 1-stage fan 0: 1 bar 1: All 3 bars | 1 | 1 | If No Fan user override, fan button will be disabled Fan Auto icon and Speed be displayed | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
74 | HVAC | l Holding | v setup | 2209 | 42210 | HV016 | R/W | 209 | NV | HVAC Mode Type Selection | enum | 0: Disabled 1: Simple (hvac mode directly selected by user) 2: Advanced (effective mode can be overridden by user) | 0 | 0 | The main difference between simple and advanced mode is how the user selection is interpreted.In advanced mode, the relevant symbol blinks to indicate that it is an override. In simple mode, the symbol will be steady. | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
75 | HVAC | l Holding | v setup | 2210 | 42211 | HV017 | R/W | 210 | NV | Available HVAC Modes | bitmap | Bit0: "AUTO" (1) Bit1: "HEAT" (2) Bit2: "COOL" (4) Bit3: "FAN ONLY" (8) Bit4: "OFF" (16) Bit5: "HTG1" (32) Bit6: "HTG2" (64) Bit7: "CLG1" (128) Bit8: "CLG2" (256) | 1 | 15 | The register defines which HVAC modes the room user can select. Example: If the room user should be able to select between Auto, Heating, Cooling, Fan Only, then the register value is 1+2+4+8=15. | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
76 | Lights | l Input | £ runtime | 300 | 30301 | LT001 | R | NA | V | Light Group 1 new level | % | 0…100% | 1 | 0x7FFF | These return to 0x7FFF when master reads them. If light group configured as on/off, any value >=1 % means ON
77 | Lights | l Input | £ runtime | 301 | 30302 | LT002 | R | NA | V | Light Group 1 new scene | int | 0-15 | 1 | 0x7FFF | These return to 0x7FFF when master reads them
78 | Lights | l Input | £ runtime | 302 | 30303 | LT003 | R | NA | V | Light Group 2 new level | % | 0…100% | 1 | 0x7FFF | These return to 0x7FFF when master reads them. If light group configured as on/off, any value >=1 % means ON
79 | Lights | l Input | £ runtime | 303 | 30304 | LT004 | R | NA | V | Light Group 2 new scene | int | 0-15 | 1 | 0x7FFF | These return to 0x7FFF when master reads them
80 | Lights | l Input | £ runtime | 304 | 30305 | LT005 | R | NA | V | Light Group 3 new level | % | 0…100% | 1 | 0x7FFF | These return to 0x7FFF when master reads them. If light group configured as on/off, any value >=1 % means ON
81 | Lights | l Input | £ runtime | 305 | 30306 | LT006 | R | NA | V | Light Group 3 new scene | int | 0-15 | 1 | 0x7FFF | These return to 0x7FFF when master reads them
82 | Lights | l Input | £ runtime | 306 | 30307 | LT007 | R | NA | V | Light Group 4 new level | % | 0…100% | 1 | 0x7FFF | These return to 0x7FFF when master reads them. If light group configured as on/off, any value >=1 % means ON
83 | Lights | l Input | £ runtime | 307 | 30308 | LT008 | R | NA | V | Light Group 4 new scene | int | 0-15 | 1 | 0x7FFF | These return to 0x7FFF when master reads them
84 | Lights | l Holding | £ runtime | 1300 | 41301 | LT009 | R/W | NA | V | Light Group 1 level feedback | % | 0…100% | 1 | 50% | Updated automatically when DALI64 is on Port 2 If DALI64 is not on port 2, Master controller needs to continuously read these from the DALI64 sensor and write to the wall module. 255 means unknown. For example, when last command to a group was scene recall, light level is unknown.
85 | Lights | l Holding | £ runtime | 1301 | 41302 | LT010 | R/W | NA | V | Light Group 1 scene feedback | int | 0-15 | 1 | 0 | Updated automatically when DALI64 is on Port 2 If DALI64 is not on port 2, Master controller needs to continuously read these from the DALI64 sensor and write to the wall module. 255 means unknown. For example, when last command to a group was scene recall, light level is unknown.
86 | Lights | l Holding | £ runtime | 1302 | 41303 | LT011 | R/W | NA | V | Light Group 2 level feedback | % | 0…100% | 1 | 50% | Updated automatically when DALI64 is on Port 2 If DALI64 is not on port 2, Master controller needs to continuously read these from the DALI64 sensor and write to the wall module. 255 means unknown. For example, when last command to a group was scene recall, light level is unknown.
87 | Lights | l Holding | £ runtime | 1303 | 41304 | LT012 | R/W | NA | V | Light Group 2 scene feedback | int | 0-15 | 1 | 0 | Updated automatically when DALI64 is on Port 2 If DALI64 is not on port 2, Master controller needs to continuously read these from the DALI64 sensor and write to the wall module. 255 means unknown. For example, when last command to a group was scene recall, light level is unknown.
88 | Lights | l Holding | £ runtime | 1304 | 41305 | LT013 | R/W | NA | V | Light Group 3 level feedback | % | 0…100% | 1 | 50% | Updated automatically when DALI64 is on Port 2 If DALI64 is not on port 2, Master controller needs to continuously read these from the DALI64 sensor and write to the wall module. 255 means unknown. For example, when last command to a group was scene recall, light level is unknown.
89 | Lights | l Holding | £ runtime | 1305 | 41306 | LT014 | R/W | NA | V | Light Group 3 scene feedback | int | 0-15 | 1 | 0 | Updated automatically when DALI64 is on Port 2 If DALI64 is not on port 2, Master controller needs to continuously read these from the DALI64 sensor and write to the wall module. 255 means unknown. For example, when last command to a group was scene recall, light level is unknown.
90 | Lights | l Holding | £ runtime | 1306 | 41307 | LT015 | R/W | NA | V | Light Group 4 level feedback | % | 0…100% | 1 | 50% | Updated automatically when DALI64 is on Port 2 If DALI64 is not on port 2, Master controller needs to continuously read these from the DALI64 sensor and write to the wall module. 255 means unknown. For example, when last command to a group was scene recall, light level is unknown.
91 | Lights | l Holding | £ runtime | 1307 | 41308 | LT016 | R/W | NA | V | Light Group 4 scene feedback | int | 0-15 | 1 | 0 | Updated automatically when DALI64 is on Port 2 If DALI64 is not on port 2, Master controller needs to continuously read these from the DALI64 sensor and write to the wall module. 255 means unknown. For example, when last command to a group was scene recall, light level is unknown.
92 | Lights | l Holding | £ runtime | 1308 | 41309 | LT037 | R/W | NA | V | Group Light State feedback | bitmap | Bit0: Group 1 is ON Bit1: Group 2 is ON Bit2: Group 3 is ON Bit3: Group 4 is ON | 1 | 0 | This Register used to display light on status feedback on wall module by turning on the respective group Lamp icon Updated automatically when DALI64 is on Port 2 If DALI64 is not on port 2, Master controller needs to continuously read these from the DALI64 sensor and write to the wall module. 255 means unknown. For example, when last command to a group was scene recall, light level is unknown.
93 | Lights | l Holding | v setup | 2300 | 42301 | LT017 | R/W | 300 | NV | Light Group Count | int | 0…4 | 1 | 2 | No of light groups. Set to zero if light control is not required. Light Button will be disabled | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
94 | Lights | l Holding | v setup | 2301 | 42302 | LT018 | R/W | 301 | NV | Light adjust step size | enum | 0 : 1% 1 : 2% 2 : 5% 3: 10% 4: 20% | 1 | 3 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
95 | Lights | l Holding | v setup | 2302 | 42303 | LT019 | R/W | 302 | NV | Light Group 1 allow dimming | enum | 0: only on/off control, 1: allow dimming | 1 | 1 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
96 | Lights | l Holding | v setup | 2303 | 42304 | LT020 | R/W | 303 | NV | Light Group 1 min level | % | 0…100% | 1 | 1% | if down key is press and hold for 1.5 Sec, group will be turned off | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
97 | Lights | l Holding | v setup | 2304 | 42305 | LT021 | R/W | 304 | NV | Light Group 1 max level | % | 0…100% | 1 | 100% |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
98 | Lights | l Holding | v setup | 2305 | 42306 | LT022 | R/W | 305 | NV | Light Group 1 number of scenes | int | 0-16 | 1 | 4 | Set to zero if Scenes are not configured Scene 1-16 corresponds to 0-15 in DALI64 when connected on Port 2 | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
99 | Lights | l Holding | v setup | 2306 | 42307 | LT023 | R/W | 306 | NV | Light Group 2 allow dimming | enum | 0: only on/off control, 1: allow dimming | 1 | 1 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
100 | Lights | l Holding | v setup | 2307 | 42308 | LT024 | R/W | 307 | NV | Light Group 2 min level | % | 0…100% | 1 | 1% | if down key is press and hold for 1.5 Sec, group will be turned off | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
101 | Lights | l Holding | v setup | 2308 | 42309 | LT025 | R/W | 308 | NV | Light Group 2 max level | % | 0…100% | 1 | 100% |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
102 | Lights | l Holding | v setup | 2309 | 42310 | LT026 | R/W | 309 | NV | Light Group 2 number of scenes | int | 0-16 | 1 | 4 | Set to zero if Scenes are not configured Scene 1-16 corresponds to 0-15 in DALI64 when connected on Port 2 | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
103 | Lights | l Holding | v setup | 2310 | 42311 | LT027 | R/W | 310 | NV | Light Group 3 allow dimming | enum | 0: only on/off control, 1: allow dimming | 1 | 1 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
104 | Lights | l Holding | v setup | 2311 | 42312 | LT028 | R/W | 311 | NV | Light Group 3 min level | % | 0…100% | 1 | 1% | if down key is press and hold for 1.5 Sec, group will be turned off | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
105 | Lights | l Holding | v setup | 2312 | 42313 | LT029 | R/W | 312 | NV | Light Group 3 max level | % | 0…100% | 1 | 100% |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
106 | Lights | l Holding | v setup | 2313 | 42314 | LT030 | R/W | 313 | NV | Light Group 3 number of scenes | int | 0-16 | 1 | 4 | Set to zero if Scenes are not configured Scene 1-16 corresponds to 0-15 in DALI64 when connected on Port 2 | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
107 | Lights | l Holding | v setup | 2314 | 42315 | LT031 | R/W | 314 | NV | Light Group 4 allow dimming | enum | 0: only on/off control, 1: allow dimming | 1 | 1 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
108 | Lights | l Holding | v setup | 2315 | 42316 | LT032 | R/W | 315 | NV | Light Group 4 min level | % | 0…100% | 1 | 1% | if down key is press and hold for 1.5 Sec, group will be turned off | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
109 | Lights | l Holding | v setup | 2316 | 42317 | LT033 | R/W | 316 | NV | Light Group 4 max level | % | 0…100% | 1 | 100% |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
110 | Lights | l Holding | v setup | 2317 | 42318 | LT034 | R/W | 317 | NV | Light Group 4 number of scenes | int | 0-16 | 1 | 4 | Set to zero if Scenes are not configured Scene 1-16 corresponds to 0-15 in DALI64 when connected on Port 2 | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
111 | Lights | l Holding | v setup | 2318 | 42319 | LT035 | R/W | 318 | NV | SceneForLightsOn | signed int | -1….15 | 1 | -1 | Used for power button functions (UI021 & UI022) -1 = no scene set, instead use 100% level as ON Command or Last light level | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
112 | Lights | l Holding | v setup | 2319 | 42320 | LT036 | R/W | 319 | NV | SceneForLightsOff | signed int | -1….15 | 1 | -1 | Used for power button functions (UI021 & 22) -1 = no scene set, instead use 0% level as OFF commands | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
113 | Blinds | l Input | £ runtime | 400 | 30401 | BL001 | R | NA | V | Blind Group 1 new position | % | 0…100% | 1 | 0 | 0=Fully up or Window is closed. Reset to 0x7FFF one read by master
114 | Blinds | l Input | £ runtime | 401 | 30402 | BL002 | R | NA | V | Blind Group 1 new angle | signed int (°) | -180°…180° | 1 | 0 | 0=Fully up or Window is closed. Reset to 0x7FFF one read by master
115 | Blinds | l Input | £ runtime | 402 | 30403 | BL003 | R | NA | V | Blind Group 2 new position | % | 0…100% | 1 | 0 | 0=Fully up or Window is closed. Reset to 0x7FFF one read by master
116 | Blinds | l Input | £ runtime | 403 | 30404 | BL004 | R | NA | V | Blind Group 2 new angle | signed int (°) | -180°…180° | 1 | 0 | 0=Fully up or Window is closed. Reset to 0x7FFF one read by master
117 | Blinds | l Holding | £ runtime | 1400 | 41401 | BL005 | R/W | NA | V | Blind Group 1 current pos. | % | 0…100% | 1 | 255 | Master controller needs to write these continuously (or on change) to the wall module. 0=Fully up or Window is closed. | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
118 | Blinds | l Holding | £ runtime | 1401 | 41402 | BL006 | R/W | NA | V | Blind Group 1 current angle | signed int (°) | -180°…180° | 1 | 255 | Master controller needs to write these continuously (or on change) to the wall module. 0=Fully up or Window is closed. | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
119 | Blinds | l Holding | £ runtime | 1402 | 41403 | BL007 | R/W | NA | V | Blind Group 2 current pos. | % | 0…100% | 1 | 255 | Master controller needs to write these continuously (or on change) to the wall module. 0=Fully up or Window is closed. | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
120 | Blinds | l Holding | £ runtime | 1403 | 41404 | BL008 | R/W | NA | V | Blind Group 2 current angle | signed int (°) | -180°…180° | 1 | 255 | Master controller needs to write these continuously (or on change) to the wall module. 0=Fully up or Window is closed. | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
121 | Blinds | l Holding | v setup | 2400 | 42401 | BL009 | R/W | 400 | NV | Blind Group Count | int | 0…2 | 1 | 1 | Set to zero if Blind is not configured Blind button will be disabled | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
122 | Blinds | l Holding | v setup | 2401 | 42402 | BL010 | R/W | 401 | NV | Blinds position adjust step size | enum | 0: 1% 1 : 2% 2 : 5% 3: 10% 4: 20% | 1 | 3 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
123 | Blinds | l Holding | v setup | 2402 | 42403 | BL011 | R/W | 402 | NV | Blinds angle adjust step size | enum | 0: 1% 1 : 2% 2 : 5% 3: 10% 4: 15% 5: 20% 6: 25% 7: 30% 8: 40% 9: 50% | 1 | 3 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
124 | Blinds | l Holding | v setup | 2403 | 42404 | BL012 | R/W | 403 | NV | Blind Group 1 Type | bitmap | Bit0: angle control 0: position only 1: position + angle Bit 1: position direct/reverse 0: reverse 1: direct | - | 1 | Direct: up button works 0->100% Reverse: up button works 100->0% | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
125 | Blinds | l Holding | v setup | 2404 | 42405 | BL013 | R/W | 404 | NV | Blind 1 position min | % | 0…100% | 1 | 0 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
126 | Blinds | l Holding | v setup | 2405 | 42406 | BL014 | R/W | 405 | NV | Blind 1 position max | % | 0…100% | 1 | 100 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
127 | Blinds | l Holding | v setup | 2406 | 42407 | BL015 | R/W | 406 | NV | Blind 1 angle min | signed int (°) | -180°…180° | 1 | -80° |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
128 | Blinds | l Holding | v setup | 2407 | 42408 | BL016 | R/W | 407 | NV | Blind 1 angle max | signed int (°) | -180°…180° | 1 | +80° |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
129 | Blinds | l Holding | v setup | 2408 | 42409 | BL017 | R/W | 408 | NV | Blind group 2 type | bitmap | Bit0: angle control 0: position only 1: position + angle Bit 1: position direct/reverse 0: reverse 1: direct | - | 1 | Direct: up button works 0->100% Reverse: up button works 100->0% | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
130 | Blinds | l Holding | v setup | 2409 | 42410 | BL018 | R/W | 409 | NV | Blind 2 position min | % | 0…100% | 1 | 0 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
131 | Blinds | l Holding | v setup | 2410 | 42411 | BL019 | R/W | 410 | NV | Blind 2 position max | % | 0…100% | 1 | 100 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
132 | Blinds | l Holding | v setup | 2411 | 42412 | BL020 | R/W | 411 | NV | Blind 2 angle min | signed int (°) | -180°…180° | 1 | -80° |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
133 | Blinds | l Holding | v setup | 2412 | 42413 | BL021 | R/W | 412 | NV | Blind 2 angle max | signed int (°) | -180°…180° | 1 | +80° |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
134 | Occupancy | l Input | £ runtime | 500 | 30501 | OC001 | R | NA | V | Effective Occupancy Mode | enum | 0: unknown 1: not used 2: occupied 3: off 4: holiday 5: unoccupied 6: standby 7: bypass | 1 | 0 | Effective Occupancy mode as displayed on wall module
135 | Occupancy | l Input | £ runtime | 501 | 30502 | OC002 | R | NA | V | Occupancy Override Status | enum | 0: not overridden 1: overridden | - | 0
136 | Occupancy | l Holding | £ runtime | 1500 | 41501 | OC003 | R/W | NA | V | Master Occupancy Mode | enum | 0: unknown 1: not used 2: occupied 3: off 4: holiday (moslty selected by user from Wall Module) 5: unoccupied 6: standby 7: bypass (moslty selected by user from Wall Module) | 1 | 0 | This comes from master controller (based on schedule and/or occupancy sensor)
137 | Occupancy | l Holding | £ runtime | 1501 | 41502 | OC004 | R/W | NA | V | User Selected Occupancy Mode | enum | 0: auto 1: not used 2: occupied 3: off 4: holiday 5: unoccupied 6: standby 7: bypass 255: Do-nothing | 1 | 0 | This normally reflects user selection/override. However, the master can also write to this to force the WM to a particular mode/override. If the TR80 receives 255=Do-nothing, then this command is ignored. This can be used, for example, to restore the Holiday Mode after Power Up by sending 4=Holiday from the controller to the wall module.
138 | Occupancy | l Holding | £ runtime | 1502 | 41503 | OC005 | R/W | NA | V | Bypass Remaining Minutes | min | 0-65535 min | 1 | 0
139 | Occupancy | l Holding | £ runtime | 1503 | 41504 | OC006 | R/W | NA | V | Holiday Remaining Days | min | 0-45 Days | 1 | 0
140 | Occupancy | l Holding | v setup | 2500 | 42501 | OC007 | R/W | 500 | NV | Occupancy Source | enum | 0: Modbus only (No Override from wall module) 1: Button Only (Simple selection between Occ/Unocc form wall module) 2: Modbus & override from button (Advanced, see OC08-OC015) | 1 | 1 | 0: Modbus only (button disabled) 1: Button only (simple mode, no override, only occupied/unoccupied switching on WM) 2: Modbus with override from button (advanced mode) | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
141 | Occupancy | l Holding | v setup | 2501 | 42502 | OC008 | R/W | 501 | NV | Holiday default days | days | 1-45 | 1 | 7 days |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
142 | Occupancy | l Holding | v setup | 2502 | 42503 | OC009 | R/W | 502 | NV | Bypass default minutes | min | 10-1440 min | 1 | 180 mins |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
143 | Occupancy | l Holding | v setup | 2503 | 42504 | OC010 | R/W | 503 | NV | Bypass time adjust step minutes | enum | 0: 10 mins 1: 20 mins 2: 30 mins 3: 60 mins | 1 | 2 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
144 | Occupancy | l Holding | v setup | 2504 | 42505 | OC011 | R/W | 504 | NV | Allowed overrides from OFF | bitmap | bit0: unused (1) bit1: unused (2) bit2: Allow override to OCCUPIED (4) bit3: Not applicable bit4: Allow override to HOLIDAY (16) bit5: Allow override to UNOCC (32) bit6: Allow override to STANDBY (64) bit7: Allow override to BYPASS (128) | 1 | 0 | These registers used to define which override are available in which occupancy mode. Short-press is automatically assigned to one of the below, in order of preference:- OCC, - UNOCC, - BYPASS | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
145 | Occupancy | l Holding | v setup | 2505 | 42506 | OC012 | R/W | 505 | NV | Allowed overrides from UNOCC | bitmap | bit0: unused (1) bit1: unused (2) bit2: Allow override to OCCUPIED (4) bit3: Allow override to OFF (8) bit4: Allow override to HOLIDAY (16) bit5: Not applicable bit6: Allow override to STANDBY (64) bit7: Allow override to BYPASS (128) | 1 | 144: HOL & BYPASS | These registers used to define which override are available in which occupancy mode. Short-press is automatically assigned to one of the below, in order of preference:- OCC, - UNOCC, - BYPASS | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
146 | Occupancy | l Holding | v setup | 2506 | 42507 | OC013 | R/W | 506 | NV | Allowed overrides from STANDBY | bitmap | bit0: unused (1) bit1: unused (2) bit2: Allow override to OCCUPIED (4) bit3: Allow override to OFF (8) bit4: Allow override to HOLIDAY (16) bit5: Allow override to UNOCC (32) bit6: Not applicable bit7: Allow override to BYPASS (128) | 1 | 148: OCC, HOL & BYPS | These registers used to define which override are available in which occupancy mode. Short-press is automatically assigned to one of the below, in order of preference:- OCC, - UNOCC, - BYPASS | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
147 | Occupancy | l Holding | v setup | 2507 | 42508 | OC014 | R/W | 507 | NV | Allowed overrides from OCC | bitmap | bit0: unused (1) bit1: unused (2) bit2: Not applicable bit3: Allow override to OFF (8) bit4: Allow override to HOLIDAY (16) bit5: Allow override to UNOCC (32) bit6: Allow override to STANDBY (64) bit7: Allow override to BYPASS (128) | 1 | 176: UNOCC, HOL & BYPS | These registers used to define which override are available in which occupancy mode. Short-press is automatically assigned to one of the below, in order of preference:- OCC, - UNOCC, - BYPASS | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
148 | Occupancy | l Holding | v setup | 2508 | 42509 | OC015 | R/W | 508 | NV | Occupancy Auto Reset | bitmap | Bit0: When master mode changes to UNOCC, cancel UNOCC override (1) Bit1: When master mode changes to UNOCC, cancel STBY override (2) Bit2 : When master mode changes to UNOCC, cancel OCC override (4) Bit3: reserved (8) Bit4 When master mode changes to OCC, cancel BYPASS override (16) Bit5: When master mode changes to OCC, cancel OCC override (32) | 1 | 55 (0x37) (11 0111) |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
148.5 | Occupancy | l Holding | v setup | 2509 | 42510 | OC016 | R/W | 509 | NV | Max User Bypass Allowed Time | min | 30-1440 min | 1 | 180 mins |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
149 | DispValues | l Holding | £ runtime | 1600 | 41601 | DSP001 | R/W | NA | V | Room Temperature (override) | °C | Normally on-board sensors are used for display. A master controller can override the on-board measurement by writing to these registers | 0.1 | 0x7FFF | These are values that the master controller can write to the wall module for display. Normally they become part of the rotating values display scheme in ready & protected modes. A raw value of 0x7FFF means the value is not available and should not be displayed (or that the internally measured value should be used, if an on-board sensor is present)
150 | DispValues | l Holding | £ runtime | 1601 | 41602 | DSP002 | R/W | NA | V | Room Humidity (override) | %Rh |  | 1 | 0x7FFF | These are values that the master controller can write to the wall module for display. Normally they become part of the rotating values display scheme in ready & protected modes. A raw value of 0x7FFF means the value is not available and should not be displayed (or that the internally measured value should be used, if an on-board sensor is present)
151 | DispValues | l Holding | £ runtime | 1602 | 41603 | DSP003 | R/W | NA | V | Room air quality (TVOC) | check DSP024 |  | 1 | 0x7FFF | These are values that the master controller can write to the wall module for display. Normally they become part of the rotating values display scheme in ready & protected modes. A raw value of 0x7FFF means the value is not available and should not be displayed (or that the internally measured value should be used, if an on-board sensor is present)
152 | DispValues | l Holding | £ runtime | 1603 | 41604 | DSP004 | R/W | NA | V | Room Carbon-dioxide (CO2) | ppm |  | 1 | 0x7FFF | These are values that the master controller can write to the wall module for display. Normally they become part of the rotating values display scheme in ready & protected modes. A raw value of 0x7FFF means the value is not available and should not be displayed (or that the internally measured value should be used, if an on-board sensor is present)
153 | DispValues | l Holding | £ runtime | 1604 | 41605 | DSP005 | R/W | NA | V | Outdoor temperature | °C (signed int) |  | 0.1 | 0x7FFF | These are values that the master controller can write to the wall module for display. Normally they become part of the rotating values display scheme in ready & protected modes. A raw value of 0x7FFF means the value is not available and should not be displayed (or that the internally measured value should be used, if an on-board sensor is present)
154 | DispValues | l Holding | £ runtime | 1605 | 41606 | DSP006 | R/W | NA | V | Outdoor relative humidity | %Rh |  | 1 | 0x7FFF | These are values that the master controller can write to the wall module for display. Normally they become part of the rotating values display scheme in ready & protected modes. A raw value of 0x7FFF means the value is not available and should not be displayed (or that the internally measured value should be used, if an on-board sensor is present)
155 | DispValues | l Holding | £ runtime | 1606 | 41607 | DSP007 | R/W | NA | V | Pressure | Pa (signed int) |  | 1 | 0x7FFF | These are values that the master controller can write to the wall module for display. Normally they become part of the rotating values display scheme in ready & protected modes. A raw value of 0x7FFF means the value is not available and should not be displayed (or that the internally measured value should be used, if an on-board sensor is present)
156 | DispValues | l Holding | £ runtime | 1607 | 41608 | DSP008 | R/W | NA | V | Air flow volume | m3/h |  | 1 | 0x7FFF | These are values that the master controller can write to the wall module for display. Normally they become part of the rotating values display scheme in ready & protected modes. A raw value of 0x7FFF means the value is not available and should not be displayed (or that the internally measured value should be used, if an on-board sensor is present)
157 | DispValues | l Holding | £ runtime | 1608 | 41609 | DSP009 | R/W | NA | V | Indoor particulates PM2.5 | ug/m3 |  | 1 | 0x7FFF | These are values that the master controller can write to the wall module for display. Normally they become part of the rotating values display scheme in ready & protected modes. A raw value of 0x7FFF means the value is not available and should not be displayed (or that the internally measured value should be used, if an on-board sensor is present)
158 | DispValues | l Holding | £ runtime | 1609 | 41610 | DSP010 | R/W | NA | V | Indoor particulates PM10 | ug/m3 |  | 1 | 0x7FFF | These are values that the master controller can write to the wall module for display. Normally they become part of the rotating values display scheme in ready & protected modes. A raw value of 0x7FFF means the value is not available and should not be displayed (or that the internally measured value should be used, if an on-board sensor is present)
159 | DispValues | l Holding | £ runtime | 1610 | 41611 | DSP011 | R/W | NA | V | Outdoor particulates PM2.5 | ug/m3 |  | 1 | 0x7FFF | These are values that the master controller can write to the wall module for display. Normally they become part of the rotating values display scheme in ready & protected modes. A raw value of 0x7FFF means the value is not available and should not be displayed (or that the internally measured value should be used, if an on-board sensor is present)
160 | DispValues | l Holding | £ runtime | 1611 | 41612 | DSP012 | R/W | NA | V | Outdoor particulates PM10 | ug/m3 |  | 1 | 0x7FFF | These are values that the master controller can write to the wall module for display. Normally they become part of the rotating values display scheme in ready & protected modes. A raw value of 0x7FFF means the value is not available and should not be displayed (or that the internally measured value should be used, if an on-board sensor is present)
161 | DispValues | l Holding | £ runtime | 1612 | 41613 | DSP013 | R/W | NA | V | Energy | KW | Unit displayed in top small digitals as text | 1 | 0x7FFF | These are values that the master controller can write to the wall module for display. Normally they become part of the rotating values display scheme in ready & protected modes. A raw value of 0x7FFF means the value is not available and should not be displayed (or that the internally measured value should be used, if an on-board sensor is present)
162 | DispValues | l Holding | £ runtime | 1613 | 41614 | DSP014 | R/W | NA | V | Energy | KWh | Unit displayed in top small digitals as text | 1 | 0x7FFF | These are values that the master controller can write to the wall module for display. Normally they become part of the rotating values display scheme in ready & protected modes. A raw value of 0x7FFF means the value is not available and should not be displayed (or that the internally measured value should be used, if an on-board sensor is present)
163 | DispValues | l Holding | £ runtime | 1614 | 41615 | DSP015 | R/W | NA | V | Reserved1 | signed int |  | 1 | 0x7FFF | These are values that the master controller can write to the wall module for display. Normally they become part of the rotating values display scheme in ready & protected modes. A raw value of 0x7FFF means the value is not available and should not be displayed (or that the internally measured value should be used, if an on-board sensor is present)
164 | DispValues | l Holding | £ runtime | 1615 | 41616 | DSP016 | R/W | NA | V | Reserved2 | signed int |  | 1 | 0x7FFF | These are values that the master controller can write to the wall module for display. Normally they become part of the rotating values display scheme in ready & protected modes. A raw value of 0x7FFF means the value is not available and should not be displayed (or that the internally measured value should be used, if an on-board sensor is present)
165 | DispValues | l Holding | £ runtime | 1616 | 41617 | DSP017 | R/W | NA | V | Reserved3 | signed int |  | 1 | 0x7FFF | These are values that the master controller can write to the wall module for display. Normally they become part of the rotating values display scheme in ready & protected modes. A raw value of 0x7FFF means the value is not available and should not be displayed (or that the internally measured value should be used, if an on-board sensor is present)
166 | DispValues | l Holding | £ runtime | 1617 | 41618 | DSP018 | R/W | NA | V | Reserved4 | signed int |  | 1 | 0x7FFF | These are values that the master controller can write to the wall module for display. Normally they become part of the rotating values display scheme in ready & protected modes. A raw value of 0x7FFF means the value is not available and should not be displayed (or that the internally measured value should be used, if an on-board sensor is present)
167 | DispValues | l Holding | £ runtime | 1618 | 41619 | DSP019 | R/W | NA | V | Custom Parameter 1 Value | signed int |  | x | 0x7FFF | These are values that the master controller can write to the wall module for display. Normally they become part of the rotating values display scheme in ready & protected modes. A raw value of 0x7FFF means the value is not available and should not be displayed (or that the internally measured value should be used, if an on-board sensor is present)
168 | DispValues | l Holding | £ runtime | 1619 | 41620 | DSP020 | R/W | NA | V | Custom Parameter 2 Value | signed int |  | x | 0x7FFF | These are values that the master controller can write to the wall module for display. Normally they become part of the rotating values display scheme in ready & protected modes. A raw value of 0x7FFF means the value is not available and should not be displayed (or that the internally measured value should be used, if an on-board sensor is present)
169 | DispValues | l Holding | £ runtime | 1620 | 41621 | DSP021 | R/W | NA | V | Reserved5 | signed int |  | 1 | 0x7FFF | These are values that the master controller can write to the wall module for display. Normally they become part of the rotating values display scheme in ready & protected modes. A raw value of 0x7FFF means the value is not available and should not be displayed (or that the internally measured value should be used, if an on-board sensor is present)
170 | DispValues | l Holding | £ runtime | 1621 | 41622 | DSP022 | R/W | NA | V | Reserved6 | signed int |  | 1 | 0x7FFF | These are values that the master controller can write to the wall module for display. Normally they become part of the rotating values display scheme in ready & protected modes. A raw value of 0x7FFF means the value is not available and should not be displayed (or that the internally measured value should be used, if an on-board sensor is present)
171 | DispValues | l Holding | v setup | 2600 | 42601 | DSP023 | R/W | 600 | NV | Home Display Parameter | enum | 0: Auto-scroll 1: ROOM_TEMP 2: SET_TEMP 3: ROOM_HUMIDITY 4: ROOM_AIR_QUALITY 5: ROOM_C02 6: PRESSURE 7: AIR_FLOW_VOLUME 8: OUTDOOR_TEMP 9: OUTDOOR_HUMIDITY 10: INDOOR_PM_2_5 11: INDOOR_PM_10 12: OUTDOOR_PM_2_5 13: OUTDOOR_PM_10 14: ENERGY_IN_KW 15: ENERGY_IN_KWH 16: ROOM_NUMBER 17: HVAC OVERRIDE STATUS 22: CUSTOM DİSPLAY PARAM 1 23: CUSTOM DISPLAY PARAM 2 | 1 | 1 | Selected parameter will be default Home parameter displayed on the Wall Module 0 = Auto scroll ( Scroll time DSP032) | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
172 | DispValues | l Holding | v setup | 2601 | 42602 | DSP031 | R/W | 601 | NV | Display Values Receive Timeout | min | 1…60 min | 1 | 5 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
173 | DispValues | l Holding | v setup | 2602 | 42603 | DSP024 | R/W | 602 | NV | TVOC unit | enum | 0: ug/m3 1: mg/m3 2: ppm 3. ppb | 1 | 0 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
174 | DispValues | l Holding | v setup | 2603 | 42604 | DSP025 | R/W | NA | NV | Custom parameter 1 text chars 1&2 | 2 x ascii | 0-255 ; 0-255 | 1 | 0x2020 | Text to be displayed in the upper screen area. Only A-Z uppercase chars, numbers, minus sign and space are supported Example: KLUX = 6b 4c 55 58 = 27468 as TextA and 21848 as TextB Example: M3/H = 6d 33 2F 68 = 27955 as TextA and 12136 as TextB | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
175 | DispValues | l Holding | v setup | 2604 | 42605 | DSP026 | R/W | NA | NV | Custom parameter 1 text chars 3&4 | 2 x ascii | 0-255 ; 0-255 | 1 | 0x2020 | Text to be displayed in the upper screen area. Only A-Z uppercase chars, numbers, minus sign, slash and space are supported | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
176 | DispValues | l Holding | v setup | 2605 | 42606 | DSP027 | R/W | NA | NV | Custom parameter 1 Text Attributes | bitmap | See CustomDisplayParamConfig sheet to configure | 1 | 0 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
177 | DispValues | l Holding | v setup | 2606 | 42607 | DSP028 | R/W | NA | NV | Custom parameter 2 text chars 1&2 | 2 x ascii | 0-255 ; 0-255 | 1 | 0x2020 | Text to be displayed in the upper screen area. Only A-Z uppercase chars, numbers, minus sign, slash and space are supported | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
178 | DispValues | l Holding | v setup | 2607 | 42608 | DSP029 | R/W | NA | NV | Custom parameter 2 text chars 1&2 | 2 x ascii | 0-255 ; 0-255 | 1 | 0x2020 | Text to be displayed in the upper screen area. Only A-Z uppercase chars, numbers, minus sign and space are supported | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
179 | DispValues | l Holding | v setup | 2608 | 42609 | DSP030 | R/W | NA | NV | Custom parameter 2 Text Attributes | bitmap | See CustomDisplayParamConfig sheet to configure | 1 | 0 |  | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y
180 | DispValues | l Holding | v setup | 2609 | 42610 | DSP032 | R/W | NA | NV | Display Values Auto scroll timing | sec | 1-30 sec | 1 | 3 s | check DSP023 to enable auto scroll | Y |  |  |  |  | Y |  |  |  |  | Y |  | Y

## CustomDisplayParamConfig
Bit 12&13: Value alignment | Bits 9-11: air quality icons | Bits 5-8: Units icons enable | Bits 3&4: basic icons enable | Bit0&1: scale
0: right align; | 0: none | 0: none | 0: none | 0: scale = 1
1: center | 1: CO2 | 1: Celsius | 1: INDOOR icon | 1: scale = 0.1
2: left align | 2: TVOC | 2: Fahrenheit | 2: SET icon | 2: scale = 0.01
| 3: PM2.5 | 3: % | 3: OUTDOOR icon | 3: scale = 0.001
| 4: PM10 | 4: %RH
5: Pa
6: m3/h
7: mg/m3
8: ug/m3
9: ppm
10: ppb
Choose below:
1 | 1 | 0 | 3 | 0
Decimal result
4632

## ChangeLog
Sr. | Date | Release | Description
1 | 2021-09-20 | 1.02.01.00 | Initial Release